##### User Manual

Python App for updating & hosting Web Pages using DDC data

Table of Contents

1. Introduction	3

1.1 Overview	3

1.2 Software Description	3

1.3 Platform Requirements	3

2. Getting Started	4

2.1 Required Applications	4

2.2 Directories & Contents	4

3. Setting up	5

3.1 Initial Setup	5

3.1.1 Dependencies & main.pyw	5

3.1.2 Excel Raw File	6

3.1.3 HTML & soup.pyw Files	7

4. Running the Program	9

4.1 Procedures	9

4.1.1 File Configuration	9

4.1.2 Launching	10

# 1. Introduction

## 1.1 Overview

This app can read and extract point information from Direct Digital Controllers (DDC) and use those values to update web pages.

## 1.2 Software Description

The software comprises four types of python files – main.pyw, soup.pyw, app.pyw, and wsgi.pyw.

The main.pyw file extracts point information from Direct Digital Controllers (DDC) and stores the values in an excel sheet.

The soup.pyw file updates specific values on the HTML web pages using the point information excel sheet generated from the DDC.

The app.pyw and wsgi.pyw files are used to create the hosting platform for the HTML web pages.

## 1.3 Platform Requirements

- Modern Operating System:

  - Windows 7 or 10

  - Mac OS X 10.11 or higher, 64-bit

  - Linux: RHEL 6/7, 64-bit

- x86 64-bit CPU (Intel/AMD architecture)

- 4 GB RAM

- 5 GB free disk space

# 2. Getting Started

## 2.1 Required Applications

Before this program can be used, the following needs to be downloaded and installed:

- Python

- Anaconda

- Visual Studio Code

## 2.2 Directories & Contents

There are several directories present in the program. The contents of each directory are listed below:

- WebApp: This is the main directory containing the python program files and all the other directories.

- Dependencies: contains all the dependencies that need to be installed for the program to run properly

- Source: contains the excel sheets – “raw” and “data”

  - Raw – this file is used to set the requirements of the data extraction process for the main.pyw file

  - Data – consists of the data extracted from the DDC using the main.pyw file

- Static: contains the CSS files, and media files for each web page

- Templates: contains the HTML file for each web page

# 3. Setting up

## 3.1 Initial Setup

To run the program, the following steps need to be completed:

### 3.1.1 Dependencies & main.pyw

- Open Anaconda Navigator, then launch VS Code and open the folder “WebApp”

- Open a new terminal, then write the following code "pip install --no-index --find-links /path to dependencies directory/ -r requirements.txt"

  - The “path to dependencies directory” is specific to the device. For example:

- In VS Code, open the main.pyw file from the WebApp folder

  - Check the LAN IP Address of the host device and update line 7 in main.pyw: bacnet = BAC0.connect(ip=' ')

  - Line 8 refers to the time interval of data extraction from the DDC. It is measured in milliseconds (ms) and shall be updated according to the user’s preference.

### 3.1.2 Excel Raw File

The raw.csv file contains the device and point list. To extract more point information from different DDCs, the raw.csv file needs to be updated accordingly.

- Add the Device Name to the first column

- Input the corresponding Object type. If the type is Analog Input, Analog Output, or Analog Value, it has to be written as analogInput, analogOutput, and analogValue, respectively.

- Finally, update the Object Instance, Object Name, and IP Address.

### 3.1.3 HTML & soup.pyw Files

To ensure that the table values on the web pages are correct, some elements must be cross-checked between the HTML and soup.pyw files.

The soup.pyw file uses data from the data.csv file.

The steps are as follows:

- The id on the HTML files must be the same as the Object Name on the data.csv file.

  - Please make sure to update the index.html file, not the new.html file

- The updating interval (ms) for the HTML file can be found on the soup.pyw file on line 12.

- The refresh time (ms) for the HTML file can be found on line 6 of the index.html file.

  - Make sure to keep the refresh time closer to the updating interval on the soup.pyw file

- The intervals (ms) of the sliders for the footer, top left section, media, and tables are 10000, 10000, 900000, and 225000.

# 4. Running the Program

## 4.1 Procedures

The procedures for running the program are listed below.

### 4.1.1 File Configuration

The following steps are to be followed to configure the python program files:

- Open the run.bat file in VS Code and check if the path to the .pyw files are correct.

- In the folder containing the .pyw files, right click on each file and select properties

  - In properties, change “Opens with” to pythonw.exe from “C:\Program Data\Anaconda3”

### 4.1.2 Launching

The following steps are to be followed to launch the WebApp:

- Launch CMD.exe from Anaconda Navigator

  - In CMD.exe, write “cd” then the path to WebApp directory

  - Then write “run.bat” to launch the python program

  - To close the program, write “kill.bat”